## Tabelle1
Terminals Alarm-System V11
for some Versions Terminals may not be in that order but relevant is the Terminal-number
Terminals Front |  | ext.Wiring | Terminals Backside |  | ext.Wiring
1 | +12V Out | 12V Output | 41 | +12V unger. | 12V Output for ext.12V Devices
2 | R7 Out NO | Output Rel.7 12V+/24V+/220V | 42 | Minus
3 | R7 In | Input Rel.7 12V+/24V+/220V | 43 | U adj + | Output Voltage 3-12V +
4 | Minus | Minus (fused) | 44 | Minus | Output Voltage 3-12V -
5 | R7 Out NC |  | 45 | +5V | Sensor Output +5V
6 |  |  | 46 | AI 2 | Sensor 2 (internal Adj-Voltage)
7 | R6 out | Output Rel.6 12V+/24V+/220V | 47 | Out + | Output Digital +
8 | R5 Out | Output Rel.5 12V+/24V+/220V | 48 | DI 1 | Digital Input 1
9 | Minus | Minus (fused) | 49 | DI 2 | Digital Input 2
10 | R5/R6 In - |  | 50 | Out + | Output Digital +
11 | +12V Out | 12V Output for Rel.5+6 | 51 | DI 3 | Digital Input 3
12 | R5/R6 In + | Input Rel.5+6 12V+/24V+/220V | 52 | DI 4 | Digital Input 4
13 | Outp. 9+ | Output 9 +12/24V; | 53 | Out + | Output Digital +
14 | Outp. 9- | Output 9 Minus; | 54 | DI 5 | Digital Input 5
15 | Outp.10+ | Output 10 +12/24V; | 55 | DI 6 | Digital Input 6
16 | Outp.10- | Output 10 Minus | 56 | Out + | Output Digital +
17 | Outp.11+ | Output 11 +12/24V | 57 | DI 7 | Digital Input 7
18 | Outp.11- | Output 11 Minus | 58 | DI 8 | Digital Input 8
|  |  | 59 | +5V | Sensor Output +5V
21 | +12V Out | 12V Output for Rel.3+4 | 60 | AI 1 | Sensor 1 (internal Batt-Voltage)
22 | R3/R4 In + | Input Rel.3+4 12V+/24V+/220V | 61 | AI 3 | Sensor 3
23 | R4 Out | Output Rel.4 12V+/24V+/220V | 62 | +5V | Sensor Output +5V
24 | R3 Out | Output Rel.3 12V+/24V+/220V | 63 | AI4 | Sensor 4
25 | Minus | Minus (fused) | 64 | AI5 | Sensor 5
26 | R3/R4 In - |  | 71 | +5V | Sensor Output +5V
27 |  |  | 72 | AI6 | Sensor 6
28 | add.Backup |  | 73 | AI7 | Sensor 7
29 |  |  | 74 | +5V | Sensor Output +5V
30 | R2 out NO | Output Rel.2 12V+/24V+/220V | 75 | AI9 | Sensor 9
31 | R2 in | Input Rel.2 12V+/24V+/220V | 76 | AI10 | Sensor 10
32 | R2 out NC |  | 77 | +5V | Sensor Output +5V
33 | Minus In |  | 78 | AI11 | Sensor 11
34 | Minus Out | Minus Out (fused) | 79 | AI12 | Sensor 12
35 | +12V Out | Output 1 Plus 12V+/24V+ | 80 | +5V | Sensor Output +5V
36 | T1 Out - | Output 1 Minus 12V-/24V- | 81 | AI13 | Sensor 13
37 | +12V In | 10-30V Transformer + | 82 | AI14 | Sensor 14
38 | Minus In Charge | 10-30V Transformer - | 83 | +5V | Sensor Output +5V
|  |  | 84 | SCL/Counter 1
|  |  | 85 | SDA/Counter 2
|  |  | 86 | Minus
|  |  | 87 | +12V regulated
|  |  | 88 | Minus | Sensor Minus
|  |  | 89 | 2.Mic + | Microphone +
|  |  | 90 | 2.Mic - | Microphone - Sensor Minus
|  |  | 91 | Speaker.+
|  |  | 92 | Speaker.- | Sensor Minus
|  |  | 93 | Telephone + | Telephone Line
|  |  | 94 | Telephone - | Telephone Line
|  |  | 95 | load Mobile | 5V for Mobile load
|  |  | 96 | Minus | Sensor Minus
|  |  | 97 | +xV
98
99
100
NO = normally open
NC = normally closed
Note on B7: NC = normally closed
Note on B10: NC = normally closed
Note on B34: NO = normally open
Note on B36: NC = normally closed