## Input_Output
Overview In / Output-List Irrigation-controller
Analogue Input | Symbol-Name + Donwload MP | use for (comment) | Unit | Terminals | Output (Transistor/Relay) | Symbol + Alarm-Text + Download MP | use for | Terminals 12V normally open | Terminals 12V normally closed | Terminals 220V Phase *
1 | AI1 U battery | Battery-Voltage | V | 59+60 | 1:Trans | 1:Load 1 | Load 1 | 35+ / 36-
2 | AI2 U Output voltage | Output Voltage | V | U Out | 2:Relay | 2:Alarm 1 |  | 30+/34 -; bridge 31-35 | 32+/34 -; bridge 31-35 | 30(NO)+31(32=NC)
3 | Analog channel 3 |  | V | 59+61 | 3:Relay | 3:Start Generator | Start motor; Rotate Y forward | 24+/25 -; bridge 21-22 |  | 22(Input)+24
4 | Analog channel 4 | Generator is running | _ | 62+63 | 4:Relay | 4:Stop Generator | Stop motor; Rotate Y backwards | 23+/25 -; bridge 21-22 |  | 22(Input)+23
5 | Analog channel 5 |  | V | 62+64 | 5:Relay | 5:Alarm 2 | Alarm 2+Rotate X forward | 8 + / 9 -; Bridge 11-12 |  | 12(Input)+8
6 | AI6: Temperature | Temperature | °C | 71+72 | 6:Relay | 6:Cooling solar | Cooling solar + Rotate X backwards | 7 + / 9 -; Bridge 11-12 |  | 12(Input)+7
7 | Analog channel 7 |  | V | 71+73 | 7:Relay | 7:Gen.Load | Generator Load | 2 + / 4 -; Bridge 1-3 | 5+/4 -; Bridge 1-3 | 2(NO)+3(5=NC)
8 | Analog channel 8 | Program-Switch | _ | internal | 8:Beep | 8:Beep | Beeper | internal
9 | AI9:Batt-Bank 2 | Battery-Bank 2 | V | 74+75 | 9:Trans | 9:Load 2 | Load 2 | Load 2
10 | AI9:Batt-Bank 3 | Battery-Bank 3 | V | 74+76 | 10:Trans | 9:Load 3 | Load 3 | Load 3
11 | AI11:ext.Load | Current external Load | A | 77+78 | 11:Trans | 9:Load 4 | Load 4 | Load 4
12 | AI12:Load3 -5 | Current Load group 2 | A | 77+79 | 12:Trans | 9:Load 5 | Load 5 | Load 5
13 | AI13:Load1+2 | Current Load group 1 | A | 80+81 | 13:Trans | 9:Load 6 | Load 6 | Load 6
14 | AI14:I Solar | Current Solar | A | 80+82 | 14:Trans | 9:Load 7 | Load 7 | Load 7
15 | AI15:U NimH | NimM-Voltage | V | internal | 15:Trans | NimH-Relay | Relay NimH charge | internal
digital Input | Symbol | use for |  | Terminals | 16:Telefon | Telephone | Telephone
101 | DI1:Rotate Base-Pos | DI1:Rotate Base-Position |  | 47+48 | 17:virtual | virt. Output 1 | virt. Output or Alarm-Text 1 | internal
102 | DI2:Stop motor 1 | DI2:Stop Motor 1 |  | 47+49 | 18:virtual | virt. Output 2 | virt. Output or Alarm-Text 2 | internal
103 | DI3:Stop motor 2 | DI3:Stop Motor 2 |  | 50+51 | 19:virtual | virt. Output 3 | virt. Output or Alarm-Text 3 | internal
104 | DI4:Emerg-Stop Mo | DI4:Emergency-Stop Motor |  | 50+52 | 20:virtual | virt. Output 4 | virt. Output or Alarm-Text 4 | internal
105 | DI5:Push-button 1 | DI5:Push-button 1 |  | 53+54 | 21:virtual | virt. Output 5 | virt. Output 5 | internal
106 | DI6:Push-button 2 | DI6:Push-button 2 |  | 53+55 | 22:virtual | virt. Output 6 | virt. Output 6 | internal
107 | DI7:Push-button 3 | DI7:Push-button 3 |  | 56+57 | 23:virtual | virt. Output 7 | virt. Output 7 | internal
108 | DI8:Push-button 4 | DI8:Push-button 4 |  | 56+58 | 24:virtual | virt. Output 8 | virt. Output 8 | internal
radio Input | Symbol | use for |  | Terminals | 31:Radio | Radio_Switch 1 | Radio-Switch 1
201 | Wind-Speed | Wind-Speed by radio | km/h | radio | 32:Radio | Radio_Switch 2 | Radio-Switch 2
202 | Temperature radio | Temperature by radio | °C | radio | 33:Radio | Radio_Switch 3 | Radio-Switch 3
203 | Humidity | Humidity by radio | % | radio | 34:Radio | Radio_Switch 4 | Radio-Switch 4
204 | Rain radio | Rain radio by radio | Pulses | radio | 35:Radio | Radio_Switch 5 | Radio-Switch 5
Counter |  |  |  |  | 36:Radio | Radio_Switch 6 | Radio-Switch 6
| Counter 1 | Counter 1 |  | 84+86 | 37:Radio | Radio_Switch 7 | Radio-Switch 7
| Counter 2 | Counter 2 |  | 85+86 | 38:Radio | Radio_Switch 8 | Radio-Switch 8
Here more Sheets! |  | Procedure
1. Enter the names for the inputs and outputs in the first sheet
2. This can be exported via the button "Export to Textfile for sending". Then it can be transmitted by the program MP_Remote and “Data” to the Metamorphosis.
3. These names will also be automatically transferred to the next Excel-sheet (Channel Overview).
4. In the Channel-Overview (next page) input the function name and description.
5. To enable the export of the data do not move any rows or columns! The size can be changed.
6. Then complete the table from left to right, using the tooltips above (red corners) for information. Yellow fields are Input-fields.
7. Each module has 2 inputs and 2 outputs.
8. The Inputs are AND-linked, that means all conditions must be fulfilled.
9. All outputs are "OR"-linked, that means, the same outputs can be controlled simultaneously in different modules.
10. There are also virtual outputs (17-24) existing.
11. If several channels are to be linked by a "AND" (if you have to check several analogue Inputs) so use for the first Channel a virtual output. And check this virtual output in the 2nd Channel (input 2).
12. The time / clock function can be combined with all other functions.
13. Weekly program (eg, Friday - Sunday) can be done with the function Pulses. Input for "all" at Pulses a value > 240.
14. Example: “all” = 245 means only Friday (5). If you Input at “on for” 67 that means Saturday (6) + Sunday (7). All together Friday … Sunday.
15. In 24V systems double the voltage values

## Channels
Presetting Universal-Channels 1-20 Solar charge controller | [12 empty] | Analogue Inp.1.1 |  | Analogue Inp.1.2 |  | Digitale Inputs |  |  | Radio-Sensor |  | Output Gr.1 |  |  | Output Gr.2 |  |  | virtuelle Output
[13 empty] | 1 | AI1 U battery | 9 | AI9:Batt-Bank 2 | 1 | DI1:Rotate Base-Pos |  | 1 | Wind-Speed | 1 | 1:Load 1 |  | 9 | 9:Load 2 |  | 17 | virt. Output 1
(at the red corners, there are Infos!) | [12 empty] | 2 | AI2 U Output voltage | 10 | AI9:Batt-Bank 3 | 2 | DI2:Stop motor 1 |  | 2 | Temperature radio | 2 | 2:Alarm 1 |  | 10 | 9:Load 3 |  | 18 | virt. Output 2
the yellow fields have to be modified | [12 empty] | 3 | Analog channel 3 | 11 | AI11:ext.Load | 3 | DI3:Stop motor 2 |  | 3 | Humidity | 3 | 3:Start Generator |  | 11 | 9:Load 4 |  | 19 | virt. Output 3
The Timer-functions can be combined with all further functions. | [12 empty] | 4 | Analog channel 4 | 12 | AI12:Load3 -5 | 4 | DI4:Emerg-Stop Mo |  | 4 | Rain radio | 4 | 4:Stop Generator |  | 12 | 9:Load 5 |  | 20 | virt. Output 4
All Outputs are "Or-Logic" that means the same Outputs can be used in several modules simultaneously without problems. | [12 empty] | 5 | Analog channel 5 | 13 | AI13:Load1+2 | 5 | DI5:Push-button 1 |  | Radio-Switch |  | 5 | 5:Alarm 2 |  | Radio-Switch |  |  | 21 | virt. Output 5
Week-Programm (Friday till Sunday) by Function Pulses | [12 empty] | 6 | AI6: Temperature | 14 | AI14:I Solar | 6 | DI6:Push-button 2 |  | 31 | Radio_Switch 1 | 6 | 6:Cooling solar |  | 33 | Radio_Switch 3 |  | 22 | virt. Output 6
for 24V double the Voltage | [12 empty] | 7 | Analog channel 7 | 15 | AI15:U NimH | 7 | DI7:Push-button 3 |  | 32 | Radio_Switch 2 | 7 | 7:Gen.Load |  | 34 | Radio_Switch 4 |  | 23 | virt. Output 7
Channel function |  | On / Off | Type | Name | Actual value | </> | Setpoint | Unit | Delay on |  | Delay off |  | Input 1 |  | Output 1 |  | Input 2 |  |  | Output 2 |  | Hysteresis |  | Timer |  |  |  | Pulses
No | Function | On / Off | Type | Short Descr. or Name of Input | Actual-Value | Actual value < / > targets | Target-value | Unit | Delay on |  | Delay off |  | Nr | Name | Nr | Name | Nr | Name | Check for 0 / 1 | No | Name | Hysteresis | Unit | from h | from min | for sec /min/ hr | sec/min/hr | on for s / m / h | s / m / hr | all | m / hr / d | n.Alarm in x min
1 | Load Shedding 1 | On | 40 | Load Shedding | x | < | 11.5 | V | 30 | s | 80 | s | 1 | Batt-Voltage | 1 | Load 1 | 0 |  | 0 | 0 |  | 1 | V | 0 | 0 | 0 | sec | 0 |  | 0 | min | 0
2 | Load Shedding 2 | On | 40 | Load Shedding | x | < | 11.3 | V | 30 | s | 80 | s | 1 | Batt-Voltage | 9 | Load 2 | 0 |  | 0 | 0 |  | 1 | V | 0 | 0 | 0 | sec | 0 |  | 0 | min | 0
3 | Load Shedding 3 | On | 40 | Load Shedding | x | < | 11.1 | V | 30 | s | 80 | s | 1 | Batt-Voltage | 10 | Load 3 | 0 |  | 0 | 0 |  | 1 | V | 0 | 0 | 0 | sec | 0 |  | 0 | min | 0
4 | Load Shedding 4 | On | 40 | Load Shedding | x | < | 10.9 | V | 30 | s | 80 | s | 1 | Batt-Voltage | 11 | Load 4 | 0 |  | 0 | 0 |  | 1 | V | 0 | 0 | 0 | sec | 0 |  | 0 | min | 0
5 | Load Shedding 5 | On | 40 | Load Shedding | x | < | 10.7 | V | 30 | s | 80 | s | 1 | Batt-Voltage | 12 | Load 5 | 0 |  | 0 | 0 |  | 1 | V | 0 | 0 | 0 | sec | 0 |  | 0 | min | 0
6 | Alarm Batt empty | On | 10 | Alarm | x | < | 10.7 | V | 30 | s | 80 | s | 1 | Batt-Voltage | 0 | _ | 0 |  | 0 | 0 |  | 1 | V | 0 | 0 | 0 | sec | 0 |  | 0 | min | 3
7 | Alarm-system over PIR Motion Sensors | Off | 74 | Alarm | x | < | 51.2 | _ | 20 | s | 60 | s | 3 | Analogously 3 | 4 | Relay 4 | 0 |  | 0 | 0 |  | 0 | _ | 0 | 0 | 0 | sec | 0 |  | 0 | min | 3
8 | Light delayed off by PIR Motion Sensors / Push-Button | Off | 4 | Alarm | x | < | 0 | _ | 0 | s | 103 | min | 0 |  | 2 | Relay 2 | 105 | Digital 5 | 0 | 0 |  | 0 | _ | 18 | 0 | 212 | Std | 0 |  | 0 | min | 0
9 | Light on PIR Motion Sensors / Push-Button | Off | 4 | Alarm | x | < | 0 | _ | 0 | s | 103 | min | 0 |  | 3 | Relay 3 | 106 | Digital 6 | 0 | 0 |  | 0 | _ | 18 | 0 | 212 | Std | 0 |  | 0 | min | 0
10 | Fridge/Deep Freeze only on daytime | Off | 4 | _ | x | < | 0 | _ | 0 | s | 0 | s | 0 |  | 6 | Relay 6 | 0 |  | 0 | 0 |  | 0 | _ | 11 | 0 | 206 | Std | 0 | s | 0 | min | 0
11 | Fridge/Deep-Freeze on if Temp > X °C | Off | 1 | _ | x | > | 10 | °C | 20 | s | 102 | min | 7 | Temp Fridge | 6 | Relay 6 | 0 |  | 0 | 0 |  | 3 | °C
12 | cooling solar-cell | Off | 1 | Temp | x | > | 40 | °C | 10 | s | 20 | s | 5 | Analog 5 | 6 | W-Pump | 0 |  | 0 | 0 |  | 5 | °C | 0 | 0 | 0 | sec | 15 | s | 10 | min | 0
13 | cleaning solar-cell | Off | 4 | Timer | x | < | 0 | _ | 0 | s | 0 | s | 0 |  | 6 | W-Pump | 0 |  | 0 | 0 |  | 0 | _ | 4 | 0 | 102 | min | 0 |  | 0 | min | 0
14 | Add.Device on with Batt.Full | Off | 0 | Batt-Voltage | x | > | 13.8 | V | 30 | s | 3 | s | 1 | Batt-Voltage | 3 | Relay 3 | 0 |  | 0 | 0 |  | 1.5 | V | 0 | 0 | 0 | sec | 0 |  | 0 | min | 0
15 | Run dry Protection pump | Off | 24 | Locking | x | < | 0 | _ | 10 | s | 80 | s | 0 |  | 6 | W-Pump | 102 | Empty | 0 | 0 |  | 0 | _ | 0 | 0 | 0 | sec | 0 |  | 0 | min | 0
16 | Wind-generator Storm protection | Off | 3 | I Solar | x | > | 30 | A | 3 | s | 103 | min | 14 | I Solar | 7 | Relay 7 | 0 |  | 0 | 0 |  | 1 | A | 0 | 0 | 0 | sec | 0 |  | 0 | min | 0
17 | Circulation-pump on solar water heating | Off | 0 | Temperature | x | > | 13.8 | V | 5 | s | 30 | s | 1 | T-Watertank | 7 | Pump | 0 |  | 0 | 0 |  | 0.5 | V | 0 | 0 | 0 | sec | 0 | s | 0 | min | 0
18 | Circulation-pump off solar water heating | Off | 21 | T-Pump off | Tank | > | 0 | °C | 30 | s | 30 | s | 9 | T-Watertank | 2 | Pump | 60 | Temp.Solar-Collector | 0 | 0 |  | 2 | °C | 0 | 0 | 0 | sec | 0 | s | 0 | min | 0
19 | Temp.Max. pump off solar water heating | Off | 21 | T-Pump off | T-Kollektor | > | 85 | °C | 10 | s | 10 | s | 9 | T-Watertank | 2 | Pump | 0 |  | 0 | 0 |  | 1 | °C | 0 | 0 | 0 | sec | 0 | s | 0 | min | 0
20 | Collector Temp min pump off | Off | 1 | Temp. | T-Kollektor | < | 30 | °C | 10 | s | 10 | s | 10 | T-Collector | 2 | Solar-pump | 0 |  | 0 | 0 |  | 2 | °C | 0 | 0 | 0 | sec | 0 | s | 0 | min | 0
below, buttons for importing and exporting of the data. Import overwrites the Data in theTable!
You need a special function? No problem, write us. We check how to realize it and and you get back the data and you only need to down-load it.
Default canal |  |  | (at the red corners, there are info!)
Channel function |  | On / Off | Type | Name | Actual value | </> | Setpoint | Unit | Delay on |  | Delay off |  | Input 1 |  | Output 1 |  | Input 2 |  |  | Output 2 |  | Hysteresis |  | Timer |  |  |  | Pulses
No | Function | On / Off | Type | Short Descr. or Name of Input | Actual-Value | Actual value < / > targets | Target-value | Unit | Delay on |  | Delay off |  | Nr | Name | Nr | Name | Nr | Name | Check for 0 / 1 | No | Name | Hysteresis | Unit | from h | from min | for sec /min/ hr | sec/min/hr | on for s / m / h | s / m / hr | all | m / hr / d | n.Alarm in x min
1 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
2 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
3 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
4 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
5 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
6 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
7 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
8 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
9 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
10 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
11 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
12 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
13 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
14 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
15 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
16 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
17 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
18 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
19 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
20 |  | From | 0 |  |  |  | 0 | _ | 5 | s | 0 | s | 0 |  | 0 |  | 0 |  |  | 0 |  |  | _ | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
wide Outputs pre-allocation | [5 empty] | wide Outputs current
Parameters | Type | Output |  |  |  | Parameters | Type | Output
53 | Add.Device one | 3 | Relay 3 |  |  | 53 | [5 empty] | This function reads the values of the controller from a text-data file (which has to be loaded with the MP_Remote function "Load Data universal-module" prior to that).
57 | Start motor | 3 | Relay 3 |  |  | 57 | [5 empty] | Caution! Above values are overwritten
58 | Stop motor | 4 | Relay 4 |  |  | 58
59 | Generator cargo | 2 | Relay 2 |  |  | 59
Transfer above Data (only the Data in the upper Block!) to the controller. Then select MP_Remote "data", "data universal-module send"
Note on B11: Switch off Load at voltage < x
Note on B12: Switch off Load at voltage < x V
Note on B13: Switch off Load at voltage < x V
Note on B14: Switch off Load at voltage < x V
Note on B15: Switch off Load at voltage< x V
Note on B20: Kühlschränke, Gefiertruhen brauchen sehr viel Strom. Es empfiehlt sich daher diese Geräte nur z.B. tagsüber bei vollem Sonnenschein einzuschalten. Meist hält die Kälte auch im ausgeschalten Zustand sehr lange. Damit kann sehr viel Energie gespart werden
Note on B21: Als Sicherheit könnte eine Temperatur-Messung in den Kühlschrank eingebaut werden, die bei kritischen Temperaturen dann in jedem Fall einschaltet.
Note on B23: only by Time
Note on B25: for cooling and cleaning
Note on B26: Windgenerator Storm-potection by I Load
Note on B27: Hat die Differenz-Temperatur einen Wert von x Grad überschritten, schaltet die Zirkulations-Pumpe ein, d.h. Tank-Temp < Solar-Temp - Hysterese. Hysterese z.B. 6-8°; Zweite Temp. wird bei Eingang 2 (51-66) angegeben. Damit wird als Sollwert Temp. 2 verwendet.
Note on B28: Hat die Differenz-Temperatur einen Wert von x Grad unterschritten, schaltet die Zirkulations-Pumpe aus, d.h. Tanktemp > Solar-Temp - Hysterese (z.B 2°); Richtet sich nach Temperatur-Verlust Solar bis Tank
Note on B29: Hat das Speicherwasser eine Höchsttemperatur von 85-90° erreicht, schaltet die Pumpe ab, um eine Überhitzung des Speichers zu verhindern
Note on B30: Hat die Kollektor-Temperatur eine minimale Temperatur von 30 Grad erreicht, schaltet die Pumpe aus, um eine Kühlung des Speichers zu verhindern.
Note on C10: 0=Off; 1=On 11=if pulse 1 active. Time Pulse 1 = Delay off 12=if pulse 2 active. Time Pulse 2 = Delay off ... 15=if pulse 5 active. Time Pulse 5 = Delay off 121-140 = The channel is only active if the according Zone in Menu 3 is active 121=group 1 enabled .... 140=group 20 enabled 142=all group < 2 enabled ...... 160=all group < 20 enabled
Note on C37: 0=Off; 1=On 11=if pulse 1 active. Time Pulse 1 = Delay off 12=if pulse 2 active. Time Pulse 2 = Delay off ... 15=if pulse 5 active. Time Pulse 5 = Delay off 121=group 1 enabled .... 140=group 20 enabled 142=all group < 2 enabled ...... 160=all group < 20 enabled
Note on C60: 1 = Load 1 2 = Relais 2 3 = Relais 3 4 = Relais 4 5 = Relais 5 6 = Relais 6 7 = Relais 7 8 = Beep 9 = Load2 10 = Load3 11 = Load4 12 = Load5 13 = Load6 14 = Load7 15 = NimH-R 17 = SW-Output 1 18 = SW-Output 2 19 = SW-Output 3 20 = SW-Output 4
Note on D10: Unit Type 0 = Batt-Voltage (V) Type 1 =°C Type 2 = % Type 3 = A Type 4 = no Unit Type 5 = bar Type 6 = l/hr Type 7 = Lux Type 8 = KW Type 9 = W Type 0-9 normal f.e.: Device > 13,8V on; off at <= 13,3 V Mains < 11,6 V on; off at >= 12,6 V 10-19 inverse Hysteresis f.e. Load on at > 12,8 V and off at<= 11,8 V. 20-29 = Interlock: switch off Output 30-39 = Impulse: just once for the time defined in Delay on 40-49 = Load shedding if Battery empty 50-59 = PI-Controller with analogue Output 12V/24V and 220V 60-69 = On / Off by Push-button 70-79 = Alarm-channel with Setpoint Time until next Alarm etc. Example 71 = Alarm with Unit °C
Note on D37: Unit Type 0 = Batt-Voltage (V) Type 1 =°C Type 2 = % Type 3 = A Type 4 = no Unit Type 5 = bar Type 6 = l/hr Type 7 = Lux Type 8 = Watt Type 0-9 normal f.e.: Device > 13,8V on; off at <= 13,3 V Mains < 11,6 V on; off at >= 12,6 V 10-19 inverse Hysteresis f.e. Load on at > 12,8 V and off at<= 11,8 V. 20-29 = Interlock: switch off Output 30-39 = Impulse: just once for the time defined in Delay on 40-49 = Load shedding if Battery empty 50-59 = PI-Controller with analogue Output 12V/24V and 220V 60-69 = On / Off by Push-button 70-79 = Alarm-channel with Setpoint Time until next Alarm etc. Example 71 = Alarm with Unit °C
Note on G10: "<" means Output on if Actual.Value < Setpoint - Hysteresis ">" means Output on if Actual.Value > Setpoint + Hysteresis "2" = compare "=" f.e.. Prog-Switch "3" = Analog-Output Setpoint manual (from SP) PID: "0" = Act > then less Output (0) "0" = Act < then less Output (0) 3 = Manual PID
Note on G37: "<" means Output on if Actual.Value < Setpoint - Hysteresis ">" means Output on if Actual.Value > Setpoint + Hysteresis
Note on I10: Typ: 0 = V 1 = °C 2 = % 3= A 4 = no Unit
Note on I37: Typ: 0 = V 1 = °C 2 = % 3= A 4 = no Unit
Note on I60: 1 = Load 1 2 = Relais 2 3 = Relais 3 4 = Relais 4 5 = Relais 5 6 = Relais 6 7 = Relais 7 8 = Beep 9 = Load2 10 = Load3 11 = Load4 12 = Load5 13 = Load6 14 = Load7 15 = NimH-R 17 = SW-Output 1 18 = SW-Output 2 19 = SW-Output 3 20 = SW-Output 4
Note on J10: <100=sec >100=min >200=hr Example: 103 = 3 min for example if the Input is not stable
Note on J37: <100=sec >100=min >200=hr Example: 103 = 3 min for example if the Input is not stable
Note on K10: sec/min/hr
Note on K37: sec/min/hr
Note on L10: <100=sec; >100=min; >200=hr Example: 203 = 3 hrs for example for a minimum Switch on Time
Note on L37: <100=sec; >100=min; >200=hr Example: 203 = 3 hrs for example for a minimum Switch on Time
Note on M10: sec/min/hr
Note on M37: sec/min/hr
Note on N10: Analog Inputs 1 = Analog 1: Battery-Voltage 2 = Analog 2 3 = Analog 3 4 = Analog 4 5 = Analog 5 6 = Analog 6 7 = Analog 7 8 = Prog-Selector 9 = U Battery-Bank 2 10 = U Battery-Bank 3 11 = ext.Current-sensor 12 = Current Load 3-5 13 = Current Load 1+2 14 = Solar-Current 15 = NimH charging voltage other Input 18 = Runtime-Value (see Param 45) 21 = Counter 1 (Input 84 + 86) 22 = Counter 2 (Input 85 + 86) 23: Freq. 1 (Terminal 84+86) 24: Freq. 2 (Terminal 85+86) Switch by SMS 90: on by SMS with Text Meta81; Off by SMS-Text Meta80 91: on by SMS with Text Meta91; Off by SMS-Text Meta90 digital Input also possible 101 = Digital 1 102 = Digital 2 103 = Digital 3 104 = Digital 4 105 = Digital 5 106 = Digital 6 107 = Digital 7 108 = Digital 8 109 = night sensor Radio sensors 201 = ELV Wind_speed 202 = ElV Temperature 203 = ElV Humidity 204 = ElV Rain
Note on N37: Analog Inputs 1 = Analog 1: Battery-Voltage 2 = Analog 2 3 = Analog 3 4 = Analog 4 5 = Analog 5 6 = Analog 6 7 = Analog 7 8 = Prog-Selector 9 = U Battery-Bank 2 10 = U Battery-Bank 3 11 = ext.Current-sensor 12 = Current Load 3-5 13 = Current Load 1+2 14 = Solar-Current 15 = NimH charging voltage other Input 16 = Minimal-Value Analog-Input 17 = Maximal-Value Analog-Input 18 = Runtime-Value Output 21 = Counter 1 (Input 84 + 86) 22 = Counter 2 (Input 85 + 86) Switch by SMS 90: on by SMS with Text Meta81; Off by SMS-Text Meta80 91: on by SMS with Text Meta91; Off by SMS-Text Meta90 digital Input also possible 101 = Digital 1 102 = Digital 2 103 = Digital 3 104 = Digital 4 105 = Digital 5 106 = Digital 6 107 = Digital 7 108 = Digital 8 109 = night sensor Radio sensors 201 = ELV Wind_speed 202 = ElV Temperature 203 = ElV Humidity 204 = ElV Rain
Note on P10: 1 = Load 1 (Transistor) 2 = Relay 2 3 = Relay 3 4 = Relay 4 5 = Relay 5 6 = Relay 6 7 = Relay 7 8 = Beeper 9 = Load 2 (Transistor) 10 = Load 3 (Transistor) 11 = Load 4 (Transistor) 12 = Load 5 (Transistor) 13 = Load 6 (Transistor) 14 = Load 7 (Transistor) 15 = NimH-loading etc 16 = Telephone Call. Telephone-number in Menu 5. Or SMS: select in Menu 8 Parameter 5 Output only for to check in another channel 17 = virtual Output 1 18 = virtual Output 2 19 = virtual Output 3 20 = virtual Output 4 21 = virtual Output 5 22 = virtual Output 6 23 = virtual Output 7 24 = virtual Output 8 25 = Start Generator 26 = Reset counter 1 27 = Reset counter 2 28 = Output Solar 29 = Output 16 30 = Reset Running Time 31 = 230 V Radio Power-Plug 1 32 = 230 V Radio Power-Plug 2 33 = 230 V Radio Power-Plug 3 34 = 230 V Radio Power-Plug 4 . 38 = 230 V Radio Power-Plug 8 41 = Alarmtext defiined as Output 17 42 = Alarmtext defiined as Output 18 ... 48 = Alarmtext defiined as Output 24 101..120 = like Output 1-20 but Output is switched invers (channel active = Relay off)
Note on P37: 1 = Load 1 (Transistor) 2 = Relay 2 3 = Relay 3 4 = Relay 4 5 = Relay 5 6 = Relay 6 7 = Relay 7 8 = Beeper 9 = Load 2 (Transistor) 10 = Load 3 (Transistor) 11 = Load 4 (Transistor) 12 = Load 5 (Transistor) 13 = Load 6 (Transistor) 14 = Load 7 (Transistor) 15 = NimH-loading etc 16 = Telephone Call. Telephone-number in Menu 5. Or SMS: select in Menu 8 Parameter 5 Output only for to check in another channel 17 = virtual Output 1 18 = virtual Output 2 19 = virtual Output 3 20 = virtual Output 4 21 = virtual Output 5 22 = virtual Output 6 23 = virtual Output 7 24 = virtual Output 8 25 Start Generator 30 = Outp.2 = Alarm-Text 31 = 230 V Radio Power-Plug 1 32 = 230 V Radio Power-Plug 2 33 = 230 V Radio Power-Plug 3 34 = 230 V Radio Power-Plug 4 101..120 = like Output 1-20 but Output is switched invers (channel active = Relay off) 121-140 = The channel is only active if the according Zone in Menu 3 is active
Note on R10: Here also check Outputs! 1 = Load 1 (Transistor) 2 = Relay 2 3 = Relay 3 4 = Relay 4 5 = Relay 5 6 = Relay 6 7 = Relay 7 8 = Beeper 9 = Load 2 (Transistor) 10 = Load 3 (Transistor) 11 = Load 4 (Transistor) 12 = Load 5 (Transistor) 13 = Load 6 (Transistor) 14 = Load 7 (Transistor) 15 = NimH-Voltage virtual Output only for to check 17 = virtual Output 1 18 = virtual Output 2 19 = virtual Output 3 20 = virtual Output 4 21 = virtual Output 5 22 = virtual Output 6 23 = virtual Output 7 24 = virtual Output 8 Analogue Input also possible (but only check =1 or =0) Analogue Input: = 51-65 (= Analogue Input 1-15) Analog Input as Value (f.e..for a Solar-Thermal System) Analogue Input = 71-80 (= Analogue Input 1-15) Switch by SMS 90: on by SMS with Text Meta81; Off by SMS-Text Meta80 91: on by SMS with Text Meta91; Off by SMS-Text Meta90 Digital Input 101 = Digital 1 102 = Digital 2 103 = Digital 3 104 = Digital 4 105 = Digital 5 106 = Digital 6 107 = Digital 7 108 = Digital 8 109 = night sensor Radio sensors 201 = ELV Wind_speed 202 = ElV Temperature 203 = ElV Humidity 204 = ElV Rain
Note on R37: Here also check Outputs! 1 = Load 1 (Transistor) 2 = Relay 2 3 = Relay 3 4 = Relay 4 5 = Relay 5 6 = Relay 6 7 = Relay 7 8 = Beeper 9 = Load 2 (Transistor) 10 = Load 3 (Transistor) 11 = Load 4 (Transistor) 12 = Load 5 (Transistor) 13 = Load 6 (Transistor) 14 = Load 7 (Transistor) 15 = NimH-Voltage virtual Output only for to check 17 = virtual Output 1 18 = virtual Output 2 19 = virtual Output 3 20 = virtual Output 4 21 = virtual Output 5 22 = virtual Output 6 23 = virtual Output 7 24 = virtual Output 8 Analogue Input also possible (but only check =1 or =0) Analogue Input: = 51-65 (= Analogue Input 1-15) Analog Input as Value (f.e..for a Solar-Thermal System) Analogue Input = 71-80 (= Analogue Input 1-15) Switch by SMS 90: on by SMS with Text Meta81; Off by SMS-Text Meta80 91: on by SMS with Text Meta91; Off by SMS-Text Meta90 Digital Input 101 = Digital 1 102 = Digital 2 103 = Digital 3 104 = Digital 4 105 = Digital 5 106 = Digital 6 107 = Digital 7 108 = Digital 8 109 = night sensor Radio sensors 201 = ELV Wind_speed 202 = ElV Temperature 203 = ElV Humidity 204 = ElV Rain
Note on T10: check " =1/=0"
Note on T37: check " =1/=0"
Note on U10: 1 = Load 1 (Transistor) 2 = Relay 2 3 = Relay 3 4 = Relay 4 5 = Relay 5 6 = Relay 6 7 = Relay 7 8 = Beeper 9 = Load 2 (Transistor) 10 = Load 3 (Transistor) 11 = Load 4 (Transistor) 12 = Load 5 (Transistor) 13 = Load 6 (Transistor) 14 = Load 7 (Transistor) 15 = NimH-loading etc 16 = Telephone Call. Telephone-number in Menu 5. Or SMS: select in Menu 8 Parameter 5 Output for to check in another channel / Alarmtext 17 = virtual Output 1 / Alarmtext 1 18 = virtual Output 2 / Alarmtext 2 19 = virtual Output 3 / Alarmtext 3 20 = virtual Output 4 / Alarmtext 4 21 = virtual Output 5 / Alarmtext 5 22 = virtual Output 6 / Alarmtext 6 23 = virtual Output 7 / Alarmtext 7 24 = virtual Output 8 / Alarmtext 8 25 = Start Generator 26 = Reset counter 1 27 = Reset counter 2 28 = Output Solar 29 = Output 16 30 = Reset Running Time 31 = 230 V Radio Power-Plug 1 32 = 230 V Radio Power-Plug 2 33 = 230 V Radio Power-Plug 3 34 = 230 V Radio Power-Plug 4 . 38 = 230 V Radio Power-Plug 8 41 = Alarmtext defiined as Output 17 42 = Alarmtext defiined as Output 18 ... 48 = Alarmtext defiined as Output 24 101..120 = like Output 1-20 but Output is switched invers (channel active = Relay off)
Note on U37: 1 = Load 1 (Transistor) 2 = Relay 2 3 = Relay 3 4 = Relay 4 5 = Relay 5 6 = Relay 6 7 = Relay 7 8 = Beeper 9 = Load 2 (Transistor) 10 = Load 3 (Transistor) 11 = Load 4 (Transistor) 12 = Load 5 (Transistor) 13 = Load 6 (Transistor) 14 = Load 7 (Transistor) 15 = NimH-loading etc 16 = Telephone Call. Telephone-number in Menu 5. Or SMS: select in Menu 8 Parameter 5 Output for to check in another channel / Alarmtext 17 = virtual Output 1 / Alarmtext 1 18 = virtual Output 2 / Alarmtext 2 19 = virtual Output 3 / Alarmtext 3 20 = virtual Output 4 / Alarmtext 4 21 = virtual Output 5 / Alarmtext 5 22 = virtual Output 6 / Alarmtext 6 23 = virtual Output 7 / Alarmtext 7 24 = virtual Output 8 / Alarmtext 8 25 Start Generator 30 = Outp.2 = Alarm-Text 31 = 230 V Radio Power-Plug 1 32 = 230 V Radio Power-Plug 2 33 = 230 V Radio Power-Plug 3 34 = 230 V Radio Power-Plug 4 101..120 = like Output 1-20 but Output is switched invers (channel active = Relay off) 121-140 = The channel is only active if the according Zone in Menu 3 is active
Note on W10: for analogue Setpoint /Actual value comparison for swtiching for example 11,8V off, 12.8V on = Hysteresis 1V
Note on W37: for analogue Setpoint /Actual value comparison for swtiching for example 11,8V off, 12.8V on = Hysteresis 1V
Note on Y10: Input Start-Time and running Time in sec/min/hrs
Note on Y37: Input Start-Time and running Time in sec/min/hrs
Note on AA10: <100=sec; >100=min; >200=hr Example: 122 = 22 min
Note on AA37: <100=sec; >100=min; >200=hr Example: 122 = 22 min
Note on AC10: <100=sec; >100=min; >200=hr 255 = Random generator week-program if "all.." > 240 then “all” = 245 means only Friday (5). If you Input at “on for” 67 that means Saturday (6) + Sunday (7). All together makes Friday … Sunday.
Note on AC37: <100=sec; >100=min; >200=hr 255 = Random generator week-program if "all.." > 240 then “all” = 245 means only Friday (5). If you Input at “on for” 67 that means Saturday (6) + Sunday (7). All together makes Friday … Sunday.
Note on AE10: <100=min; >100=hrs; >200=day > 240 = Weekprogram, last digit= weekday f.e.: Friday (=5) z.B. 245 = friday
Note on AE37: <100=min; >100=hrs; >200=day > 240 = Weekprogram, last digit= weekday f.e.: Friday (=5) z.B. 245 = friday
Note on AG10: Waiting time to next Alarm
Note on AG37: Waiting time to next Alarm

## Terminals
Electrical Connections for the Solar-charge-controller
Terminal Front side |  | ext.Wiring | Terminal Backside |  | ext.Wiring
1 | +12V Out | Bridge to 2 for 12V | 41 | +12V unger. | für Moving-Detektor 12V+
2 | R7 out NO | Load Gen (12V/24/220V)/Timer | 42 | Minus | Moving-Detektor Minus
3 | R7 in | 12V/24/220V Input (12V from Terminal 1) | 43 | U adj + | Output 3-12V +
4 | Minus | Minus (for 12V/24V) | 44 | Minus | Output 3-12V -
5 | R7 out NC |  | 45 | +5V
6 |  |  | 46 | AI 2 | intern (Spg-Reg)
7 | R6 out | Cooling Panel/Rotate Vertical.+ | 47 | Out + | Output 5V for Inputs (Door-Alarm)
8 | R5 out | Alarm 4 /Rotate Vertical - | 48 | DI 1 | Start/Stop Motor/Base-Position Tracking horizontal
9 | Minus | Bridge to 10 for Rotate 12V Motor | 49 | DI 2 | Start Motor/Final Position Tracking horiz./Empty-Signal Water-Tank
10 | R5/R6 in - | Bridge to 9 for Rotate 12V Motor | 50 | Out + | Output 5V for Inputs (Generator etc)
11 | +12V | Bridge to 12 for 12V Devices | 51 | DI 3 | Stop Motor 1 (0-active) Emergency Load on/Base Position Tracking vertical
12 | R5/R6 in + | 12V/24/220V Input (12/24V from Terminal 11) | 52 | DI 4 | Stop Motor 2 (0-active) /Send SMS by Switch/Final Position Track vertical
13 |  |  | 53 | Out + | Output Theft-Alarm 2 +
14 |  |  | 54 | DI 5 | Theft-Alarm Input 1
15 |  |  | 55 | DI 6 | Theft-Alarm Input 2
16 |  |  | 56 | Out + | Output Theft-Alarm 3 + 4
17 |  |  | 57 | DI 7 | Theft-Alarm Input 3
18 |  |  | 58 | DI 8 | Theft-Alarm Input 4
|  |  | 59 | +5V
21 | +12V Out | Bridge to 22 for 12V | 60 | AI 1 | internal (U Batt)
22 | R3/R4 in + | 12V/24/220V Input (12V from Terminal 5) | 61 | AI 3 | Moving-Detektor Signal
23 | R4 out | Stop Motor/Alarm 1 Out (Lamp/High Voltage-Unit)+/Rotate Horizont.+ | 62 | +5V | Output 5V Temp.Solarcell
24 | R3 out | Start Motor/Additional Device +//Rotate Horizont.-/Alarm 3 | 63 | AI4 | Feedback Generator running (max.5V)
25 | Minus | additional Device -/Alarm 1 - (fused) | 64 | AI5 | Input Temp.Solarcell
26 | R3/R4 in - |  | 71 | +5V | (internal: NTC)
27 | free |  | 72 | AI6 | (internal: NTC)
28 | add.Backup |  | 73 | AI7
29 |  |  | 74 | +5V
30 | R2 out NO | Alarm 2 Out | 75 | AI9
31 | R2 in | 12V/24/220V Input (12V from Terminal 35) | 76 | AI10
32 | R2 out NC |  | 77 | +5V
33 | Minus In | Minus In (no Battery charge) | 78 | AI11 | external Current-Measuring +
34 | Minus | Minus Out (fused) | 79 | AI12
35 | +12V Out |  | 80 | +5V | Current-Counter +5V
36 | T1 Out - |  | 81 | AI13
37 | +12V In | Transformer 12-30V + | 82 | AI14
38 | Minus | Transformer Minus (w.Batt. Charge) | 83 | +5V
|  |  | 84 | SCL/Counter 1 | Counter 1 Input
|  |  | 85 | SDA/Counter 2 | Counter 2 Input
|  |  | 86 | Minus | external Current-Measuring -/Counter
|  |  | 87 | +12V regulated
|  |  | 88 | Minus
|  |  | 89 | 2.Mic +
|  |  | 90 | 2.Mic -
|  |  | 91 | Speaker.+
|  |  | 92 | Speaker.-
|  |  | 93 | Telephone + | Telephone + (look Polarity!)
|  |  | 94 | Telephone - | Telephone - (look Polarity!)
|  |  | 95 | +5V | 5V ELV Radio-modul
|  |  | 96 | Minus | Minus ELV Radio-modul
|  |  | 97 | Input ELV | Input ELV Radio-modul
|  |  | 98 | Sensor Out 5V
|  |  | 99 | +12V | GSM-Modem Plus
|  |  | 100 | Minus | GSM-Modem Minus
Relais 1: Load Channel 1 (up to 3A)
Relais 2:Motor Load / Solar Channel 1 (up to 3A)
Relais 3: Solar Channel 2 / Start Motor / Additional Device if Battery full
Relais 4: Solar Channel 3 / Stop Motor / external Alarm-horn Output / Load Channel 5
Relais 5: Solar Channel 4 / Alarm-Lamp / High Voltage-Protection / Rotate backward / Load Channel 4
Relais 6: Solar Channel 5 /Cooling Panel/Rotate forward / Load Channel 3
Relais 7: Output Timer / Load Channel 2
Note: Solar Channels only for Relais-Version; If Generator-Function on, Relais 2,3,4 is used
NO = normally open
NC = normally closed